{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["MM80LMZMOD"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"MM80LMZMOD","index":0,"n_rows":36,"n_cols":7,"rows_kept":36,"cut":false,"hidden":false,"merged":[[0,0,0,6],[3,0,3,6]],"flags":["formulas_cached_only"]}
["Table Modbus  "]
["MM80LMZMOD : Compteur électrique modulaire monophasé 80 A certifié MID Modbus RS485"]
[]
["Paramètre par défaut "]
["Baud :",null,9600]
["Adresse Modbus en décimal :",null,"3 dernier chiffres du numéro de série"]
["Parité :",null,"EVEN"]
["Stop Bit :",null,1]
["Data Bit :",null,8]
["Modbus register address","R/W","Register length","Data Description","Unit","Content","Remark"]
["0000","R/W",2,"HEX data",null,"Serial number","00000000-99999999"]
["0002","R/W",1,"HEX data",null,"Modbus address","1-247 Défaut : 3 dernier chiffres du numéro de série"]
["0003","R/W",1,"HEX data",null,"Baud rate","9600=25 80; 4800=12 C0; 2400=09 60; 1200=04 B0; Défaut : 9600 Bauds"]
["0004","R",2,"Float data ",null,"SW version"]
["0006","R",2,"Float data ",null,"HW version"]
["0009","R/W",2,"Float data ",null,"SO output","1000 / 100 / 10 / 1   Défaut : 1000 imp/kWh"]
["000B","R/W",1,"HEX data",null,"Measurement way ","01 (Total= forward) / 05 (Total =forward +reverse) / 09 (Total =forward -reverse ) Défaut 09"]
["000D","R/W",1,"HEX data",null,"Vitesse de défilement","Défaut : 5 secondes"]
["000E","R",2,"Float data ","0.001V","Phase a voltage"]
["0014","R",2,"Float data ","0.01Hz","Fréquence"]
["0016","R",2,"Float data ","0.001A","Intensité"]
["001C","R",2,"Float data ","0.001kw","Total active power"]
["0024","R",2,"Float data ","0.001kvar","Total reactive power"]
["002C","R",2,"Float data ","0.001kva","Total apparent power"]
["0034","R",2,"Float data ",0.01,"Total Power factor"]
["003C","R/W",1,"Can be read separately, but must be written together; BCD code","00 00","Seconds, minutes"]
["003D","R/W",1,"Can be read separately, but must be written together; BCD code","00 00","Hour,week"]
["003E","R/W",1,"Can be read separately, but must be written together; BCD code","00 00","Date, month "]
["003F","R/W",1,"Can be read separately, but must be written together; BCD code","00 00 ","Year, null"]
["0041","R",1,"Code BCD",null,"CRC "]
["0100","R",2,"Read: float data; write: A5 EC 00F(clear all energy )","0.001kwh","Total active energy"]
["0108","R",2,"Float data ","0.001kwh","Total forward active energy "]
["0110","R",2,"Float data ","0.001kwh","Total reverse active energy "]
["0118","R",2,"Float data ","0.001kvarh","Total Reative energy"]
["0120","R",2,"Float data ","0.001kvarh","Total Forward reactive energy "]
["0128","R",2,"Float data ","0.001kvarh","total reverse reactive energy "]